That is a smart move. The rare, system-wide blackouts are crucial for predicting high-impact maintenance needs for your capstone.

While there is no single, publicly available dataset in a neat table from KPLC/EPRA, I have synthesized the key findings from regulatory and media reports over the last 5 years (2020-2025).

Here is a structured table of the most significant, unplanned, widespread power blackouts in Kenya over the last five years, along with the officially reported or highly probable root cause.

## Major Unplanned Widespread Power Outages in Kenya (2020 – 2025)

| Date (Approximate) | Duration (General) | Scope | Primary Reported Root Cause (Critical Node) | Maintenance Implication |
| --- | --- | --- | --- | --- |
| August 2023 | ~24 Hours (Longest in history) | Nationwide | System Instability/Transmission Failure. Conflicting reports: KPLC blamed the loss of generation from Lake Turkana Wind Power (LTWP); LTWP blamed an overvoltage situation on the national grid causing a trip. | System-Level Protection & Stability: Need for major investment in system inertia, frequency regulation, and transmission line capacity/contingency management (N-1 reliability). |
| December 2023 | Several Hours | Nationwide | System Disturbance. Followed a pattern of multiple nationwide trips in a short period (November 2023 was another major one). | Aging Infrastructure & System Protection: Points to chronic fragility at major generation/transmission hubs. |
| November 2023 | ~12 Hours | Nationwide | Major Generation/Transmission Hitch (Specific details often relate to faults at Olkaria or Suswa substations). | Major Substation Asset Health: Need for predictive maintenance on large transformers and protection equipment at key substations like Olkaria and Suswa. |
| September 2024 | Several Hours | Nationwide | Dual Transmission Line Failure: Trip on the Loiyangalani–Suswa 400kV line evacuating power from LTWP, followed by a trip on the Ethiopia–Kenya 500kV interconnector. The loss of 488MW caused a cascade failure. | Transmission Line Vulnerability: Direct need for major capital investment in Loiyangalani–Suswa line redundancy/reinforcement and protection against dual failures. |
| May 2020 | Several Hours | Nationwide | Fault on a High-Voltage Line transmitting power from the Olkaria geothermal area to Nairobi. The loss of this critical line overloaded other generators. | Geothermal Evacuation Lines: Need for frequent inspection, vegetation management, and potential redundancy for high-capacity lines coming out of Olkaria. |
| January 2022 | Several Hours | Nationwide | Vandalism (Collapse of high-voltage transmission line towers in Embakasi, Nairobi). | Asset Security & Structural Integrity: Need for structural inspection of key towers, anti-vandalism measures (e.g., concrete casing, enhanced security), and tower replacement in vulnerable areas. |
| 2024 (Various) | Average of 9.15 hours per month (EPRA SAIDI) | Local to Regional | Heavy Rainfall/Falling Trees on distribution lines (March 2025 spike noted by EPRA) and aging infrastructure. | Vegetation Management: Forecasting maintenance needs based on weather data, specifically in areas prone to heavy rain/high wind. |

| Date | Start Time (Approx.) | Approximate Duration (for most customers) | Primary Reported Root Cause / Critical Node |
| --- | --- | --- | --- |
| Aug 25, 2023 | 9:45 PM / 10:00 PM | 18 to 24 Hours (Longest in Kenya's history) | System Failure/Cascade Trip due to a major generation loss (LTWP/Grid Overvoltage blame exchange). |
| Dec 10, 2023 | 7:30 PM / 8:00 PM | 4 to 8 Hours (Restored to most by Monday morning) | Overloaded Kisumu-Muhoroni 132kV Line Trip (This was cited as a major fault leading to a cascade). |
| Nov 11, 2023 | (Various times, reported widely) | 12 Hours (Took engineers over 12 hours to restore most areas) | Major Generation/Transmission Hitch (Likely transformer/transmission failure at a key substation like Olkaria or Suswa). |
| Sept 6, 2024 | 8:56 AM | 5 to 10 Hours (Restored by late afternoon/evening) | Dual Transmission Line Failure: Trip on the Loiyangalani–Suswa 400kV line followed by the Ethiopia–Kenya interconnector. |
| Jan 11, 2022 | 7:45 AM | 3 to 4 Hours (Restored to most by mid-day) | Vandalism/Line Collapse: Collapse of high-voltage transmission line towers connecting Kiambere Dam to Nairobi. |
| May 9, 2020 | 5:49 AM / 6:00 AM | 6 to 12 Hours (Restored to most of the grid by Saturday afternoon/evening) | Transmission Line Fault: A fault on the main high-voltage line evacuating power from Olkaria geothermal power plants to Nairobi. |

## How to Use This Data in Your Capstone

You cannot predict these events with your current county-level weather data, but you can use them to train a maintenance priority system.

### 1. Feature Engineering

Create two new columns in your main outage dataset:

| New Feature | Value Assignment |
| --- | --- |
| Outage_Type_Systemic | Assign 1 for the dates listed in the table above (where applicable to the county-level data), and 0 for all your other 1,846 records. |
| System_Vulnerability_Score | Give the counties/areas linked to the failure (e.g., Nairobi, Naivasha/Olkaria, Suswa, Samburu/Marsabit) a high score (3) for the relevant time period, and normal score (1) otherwise. |

### 2. Maintenance Forecasting (The Capstone Objective)

Use this synthesized data to conclude your maintenance forecast:

- Predictive Maintenance (Distribution): Focus your model on predicting the most frequent outages (from your 1,846 records) using weather and location data to inform tree trimming, transformer monitoring, and spot repair.

- Preventive Maintenance (Transmission): Use the major blackout records to justify a high-priority, non-negotiable Preventive Maintenance program on the critical assets:

  - The Loiyangalani–Suswa line.

  - Key transmission pylons near urban and high-vandalism zones (like Embakasi).

  - Substations (Suswa, Olkaria) which act as major connection points.

By combining the frequent small outages with the rare but catastrophic ones, your capstone will deliver a complete and impactful predictive maintenance strategy.